MEITAVTEC LTD, 03/02/2010 14:31:05,  PIC18F4620

OBJECT LIST FOR CTU2501 CP H3 09104401

BACnet MSTP,Baud 9600...76800,n,8,1

| N° | Object | Value | Object Name | Default | Type |
| --- | --- | --- | --- | --- | --- |
| 0 | Analog Input #0 | 7...32 °C | T1_RoomTemperature | °C |  |
| 1 | Analog Input #1 | -40...89 °C | T2_ChangeOverSensorTemperature | °C |  |
| 2 | Analog Input #2 | -40...89 °C | T3_IndoorCoilTemperature | °C |  |
| 3 | Analog Input #3 | 0...100 % | AI1_Input | 0 % |  |
| 4 | Analog Input #4 | 0...100 % | AI2_Input | 0 % |  |
| 5 | Analog Output #0 | 0...10 V | AO1 | 0 V |  |
| 6 | Analog Output #1 | 0...10 V | AO2_Cooling | 0 V |  |
| 7 | Analog Value #0 | 0...3 | Mode | 1 | R/W |
| 8 | Analog Value #1 | 0...3 | FanSpeed | 1 | R/W |
| 9 | Analog Value #2 | 10...30 °C | SetPoint | 21 °C | R/W |
| 10 | Analog Value #3 | 10...30 °C | SetPointLimitCool | 10 °C | R/W |
| 11 | Analog Value #4 | 10...30 °C | SetPointLimitHeat | 30 °C | R/W |
| 12 | Analog Value #5 | 0...5 °C | DeadZoneForCool | 1 °C | R/W |
| 13 | Analog Value #6 | 0...5 °C | DeadZoneForHeat | 1 °C | R/W |
| 14 | Analog Value #7 | -6...6 °C | ReturnAirSensorCalibration | 0 °C | R/W |
| 15 | Analog Value #8 | 0...100 % | ProportionalLimitOn | 30 % | R/W |
| 16 | Analog Value #9 | 0...100 % | ProportionalLimitOff | 10 % | R/W |
| 17 | Analog Value #10 | 0...100 % | CoolIndication | 0 % | R/W |
| 18 | Analog Value #11 | 0...10 °C | CoolProportionalBand | 2 °C | R/W |
| 19 | Analog Value #12 | 0...100 % | CoolProportionalHighLimit | 100 % | R/W |
| 20 | Analog Value #13 | 0...100 % | CoolProportionalLowLimit | 0 % | R/W |
| 21 | Analog Value #14 | 0...300 | DelayStoppingFanInHeat | 30 | R/W |
| 22 | Analog Value #15 | 0...3600 sec | DelaySwitchingToUnOccupiedMode | 1200 sec | R/W |
| 23 | Analog Value #16 | 0...3600 sec | DelaySwitchingToOccupiedMode | 0 sec | R/W |
| 24 | Analog Value #17 | 0...1 | UnOccupancyModeSelect | 0 | R/W |
| 25 | Binary Input #0 | 1-On,0-Off | OccupancySensor |  |  |
| 26 | Binary Output #0 | 1-On,0-Off | BO1 | Off |  |
| 27 | Binary Output #1 | 1-On,0-Off | BO2 | Off |  |
| 28 | Binary Output #2 | 1-On,0-Off | FanLow | Off |  |
| 29 | Binary Output #3 | 1-On,0-Off | FanMedium | Off |  |
| 30 | Binary Output #4 | 1-On,0-Off | FanHigh | Off |  |
| 31 | Binary Output #5 | 1-On,0-Off | HEAT1 | Off |  |
| 32 | Binary Output #6 | 1-On,0-Off | HEAT2 | Off |  |
| 33 | Binary Output #7 | 1-On,0-Off | HEAT3 | Off |  |
| 34 | Binary Value #0 | 1-On,0-Off | OnOff | Off | R/W |
| 35 | Binary Value #1 | 1-On,0-Off | UnOccupancy | Off | R |
| 36 | Binary Value #2 | 1-On,0-Off | Celsius | On | R/W |
| 37 | Binary Value #3 | 1-On,0-Off | AutoFan | Off | R/W |
| 38 | Binary Value #4 | 1-On,0-Off | RestoreDefault | Off | R/W |
| 39 | Binary Value #5 | 1-On,0-Off | DisableOccupancySensor | Off | R/W |
| 40 | Binary Value #6 | 1-On,0-Off | OccupancySensorPolarity | Off | R/W |
| 41 | Binary Value #7 | 1-On,0-Off | ThermostatOccupancyStatus | Off | R |
| 42 | Binary Value #8 | 1-On,0-Off | LockRoomModule | Off | R/W |
| 43 | Binary Value #9 | 1-On,0-Off | LockRoomModuleMode | Off | R/W |
| 44 | Binary Value #10 | 1-On,0-Off | LockRoomModuleSetPoint | Off | R/W |
| 45 | Binary Value #11 | 1-On,0-Off | LockRoomModuleFanSpeed | Off | R/W |
| 46 | Binary Value #12 | 1-On,0-Off | LockRoomModuleOnOff | Off | R/W |